Quest 225 Compressor GMCC conversion

Overview: The Quest 225 originally made with a Rechi or LG brand compressor requires some modifications to install the available GMCC brand compressor.

Parts:

- 4043474 COMPRESSOR

- 4037332 SUCTION TUBE

- 4043476 TERMINAL COVER

- 4043477 GASKET

- 4020530 GROMMET X3

- 4020531 SLEEVE X3

- 4033032-04 CAPACITOR

- 4031519 P-CLAMP

- 1154006 BOLT SHORT X6

- 1154014 BOLT LONG x3

- 1282497 WASHER X 4

- 1107004 ¼-20 SCREW X 7

Tools:

- Needle Nose Pliers

- ¼ Hex Bit

- 5/16 Hex Bit

- 3/8 Hex Bit

- 7/16 Hex Bit

- 3/16 Drill Bit

- Drill

- Pipe cutter

Instructions:

- Disconnect power from unit.

- Using pliers grab the black humidity control knob and pull off. (Red Arrow)

- Remove the 4 - 5/16 hex screws near the corners of the electrical box cover. (Red Circle)

- Remove electrical box cover.

- Remove these screws to remove the rear angled panel and top cover.

- Remove compressor cover panel by unscrewing 2 wingnuts.

- Remove 4 screws that hold in fan assembly and p-clamp for harness (red arrow).

- Remove fan assembly from the unit.

- Remove nut holding cap on top of compressor. Remove cap and wires. Save nut.

- Remove side panel by drill 7 rivets

- Locate brass access valve on suction line and recover any remaining refrigerant.

- Remove suction line p-clamp at evaporator coil. Save plastic washer located behind p-clamp.

- Remove defrost t-stat from suction line if present. (7/21 and older)

- Un-braze compressor, suction line and access port. Save access port but discard process stub, compressor, and suction line.

- Remove compressor from unit. Discard Grommets, sleeves, bolts, cap and gasket.

- If present remove original compressor adapter plate.

- Install new compressor adapter plate using short 3/8” bolts. 3-6 bolts will used depending on the inserts in drain pan available.

- Install new grommet and sleeves on compressor.

- Install compressor using 3 long bolts and 4 washers into new inserts. The rear bolt has 2 washers for clearance.

- Make sure the compressor is not hitting fan shroud or evaporator. If so, loosen the plate and/or compressor mounting bolts to reposition. There is some adjustment built into the holes to shift the compressor position.

- Adjust discharge line by cutting off some of the tube (yellow arrow). Adjust length so that the tubes pass thru grommet correctly (red arrow). See above picture.

- Braze in new compressor using new suction line and access port as shown. See Above picture.

- Install defrost t-stat on suction line if present. Black tape not required.

- Install p-clamp and rivet on suction to evaporator coil.

- Evacuate, vacuum down and charge unit to specification on serial tag.

- Using new cap, overload and gasket install wires on compressors. Note R & S location may be swapped. No overload on this compressor

  - Red to R

  - Yellow to S

  - Black to C

- Remove old Compressor Capacitor and install new Compressor Capacitor with new P-clamp.

- Re-Install fan assembly and panels in reverse order. Use ¼ -20 self-threading screws in place of rivets.

- Repair complete